## Sheet1
| Prop_PID_Number | Prop_PID_Element | sPID | Tag_Number_Definition | SWM | SWM_Nr | Cx1 | Cx1_Nr | Cx2 | Cx2_Nr | Cx3 | Cx3_Nr | Cx4 | Cx4_Nr | Element_Description
0 | 1.1 | ['M', 'SC', 'V', 'XA'] | 1.100 | Intake air fan | S_MOTOR1 | 1
1 | 1.108 | ['PDI'] | 1.108 | Diferential pressure sensor | S_LIMIT_HI_LO | 1
2 | 1.15 | ['M', 'SC', 'TSA+', 'V'] | 1.150 | Exhaust air fan | S_DRIVE | 1 | S_MOTOR1 | 2 | S_REG_CONT | 1 | S_LIMIT_HI_LO | 26
3 | 1.158 | ['PDI'] | 1.158 | Diferential pressure sensor | S_LIMIT_HI_LO | 2
4 | 1.16 | ['M', 'SC', 'V', 'XA'] | 1.160 | Exhaust air fan | S_MOTOR1 | 3
5 | 1.2 | ['M', 'SC', 'V', 'XA'] | 1.200 | Recirculation fan | S_MOTOR1 | 4
6 | 1.208 | ['PDI'] | 1.208 | Diferential pressure sensor | S_LIMIT_HI_LO | 3
7 | 1.21 | ['M', 'SC', 'V', 'XA'] | 1.210 | Recirculation fan | S_MOTOR1 | 5
8 | 1.218 | ['PDI'] | 1.218 | Diferential pressure sensor | S_LIMIT_HI_LO | 4
9 | 1.24 | ['M', 'SC', 'V', 'XA'] | 1.240 | Recirculation fan | S_MOTOR1 | 6
10 | 1.248 | ['PDI'] | 1.248 | Diferential pressure sensor | S_LIMIT_HI_LO | 5
11 | 1.3 | ['FA-', 'QIA+', 'XA'] | 1.300 | Particle counter | S_PMS_MODBUS_TCP | 1
12 | 1.304 | ['M', 'P'] | 1.304 | Vacuum pump | S_ELMT_ON_OFF | 1
13 | 1.305 | ['GSA+', 'GSA-', 'V', 'Y'] | 1.305 | 3-way valve | S_VALVE_FLAP | 1
14 | 1.308 | ['FSA-'] | 1.308 | Flow-Switch | S_LIMIT_SWITCH | 1
15 | 1.31 | ['FA-', 'QIA+', 'XA'] | 1.310 | Particle counter | S_PMS_MODBUS_TCP | 2
16 | 1.314 | ['M', 'P'] | 1.314 | Vacuum pump | S_ELMT_ON_OFF | 2
17 | 1.315 | ['GSA+', 'GSA-', 'V', 'Y'] | 1.315 | 3-way valve | S_VALVE_FLAP | 2
18 | 1.318 | ['FSA-'] | 1.318 | Flow-Switch | S_LIMIT_SWITCH | 2
19 | 1.32 | ['FA-', 'QIA+', 'XA'] | 1.320 | Particle counter | S_PMS_MODBUS_TCP | 3
20 | 1.324 | ['M', 'P'] | 1.324 | Vacuum pump | S_ELMT_ON_OFF | 3
21 | 1.325 | ['GSA+', 'GSA-', 'V', 'Y'] | 1.325 | 3-way valve | S_VALVE_FLAP | 3
22 | 1.328 | ['FSA-'] | 1.328 | Flow-Switch | S_LIMIT_SWITCH | 3
23 | 1.33 | ['FA-', 'QIA+', 'XA'] | 1.330 | Particle counter | S_PMS_MODBUS_TCP | 4
24 | 1.334 | ['M', 'P'] | 1.334 | Vacuum pump | S_ELMT_ON_OFF | 4
25 | 1.335 | ['GSA+', 'GSA-', 'V', 'Y'] | 1.335 | 3-way valve | S_VALVE_FLAP | 4
26 | 1.338 | ['FSA-'] | 1.338 | Flow-Switch | S_LIMIT_SWITCH | 4
27 | 1.35 | ['P', 'XA'] | 1.350 | Air sampler | S_AAS_MAS_TCP | 1
28 | 1.36 | ['P', 'XA'] | 1.360 | Air sampler | S_AAS_MAS_TCP | 2
29 | 1.37 | ['P', 'XA'] | 1.370 | Air sampler | S_AAS_MAS_TCP | 3
30 | 1.4 | ['GIA+', 'GIA-', 'M', 'SC', 'XA'] | 1.400 | Automatic Mousehole
31 | 1.41 | ['GIA+', 'GIA-', 'M', 'SC', 'XA'] | 1.410 | Automatic Mousehole
32 | 1.5 | ['GSA+', 'GSA-', 'K', 'Y'] | 1.500 | Supply air flap | S_VALVE_FLAP | 5
33 | 1.51 | ['GSA+', 'GSA-', 'K', 'Y'] | 1.510 | Flap | S_VALVE_FLAP | 6
34 | 1.52 | ['GSA+', 'GSA-', 'K', 'Y'] | 1.520 | Flap | S_VALVE_FLAP | 7
35 | 1.55 | ['GIA', 'K', 'Y', 'YC'] | 1.550 | Exhaust air flap | S_MOTOR1 | 7 | S_LIMIT_HI_LO | 6
36 | 1.555 | ['GIA', 'V', 'Y', 'YC'] | 1.555 | Exhaust bypass valve | S_MOTOR1 | 8 | S_LIMIT_HI_LO | 7
37 | 1.558 | ['PDIS'] | 1.558 | Diferential pressure sensor | S_LIMIT_HI_LO | 8
38 | 1.56 | ['GIA', 'K', 'Y', 'YC'] | 1.560 | Exhaust air flap | S_MOTOR1 | 9 | S_LIMIT_HI_LO | 9
39 | 1.568 | ['PDIS'] | 1.568 | Diferential pressure sensor | S_LIMIT_HI_LO | 10
40 | 1.57 | ['GSA+', 'GSA-', 'K', 'Y'] | 1.570 | Flap | S_VALVE_FLAP | 8
41 | 1.651 | ['M', 'P'] | 1.651 | Circulating pump | S_ELMT_ON_OFF | 5
42 | 1.655 | ['H', 'M', 'NC'] | 1.655 | Control valve | S_MOTOR1 | 10 | S_REG_CONT | 2 | S_LIMIT_HI_LO | 11
43 | 1.68 | ['EC', 'TSA+'] | 1.680 | Electric heating | S_MOTOR1 | 11 | S_REG_CONT | 3 | S_LIMIT_HI_LO | 11
44 | 1.688 | ['TIC'] | 1.688 | Temperature sensor | S_LIMIT_HI_LO | 11
45 | 1.69 | ['T', 'XA'] | 1.690 | Dryer / Humidifier | S_LIMIT_ON_OFF | 1 | S_LIMIT_HI_LO | 16
46 | 1.7 | ['M', 'P', 'SC'] | 1.700 | Peristaltic pump | S_PUMP_TEST | 1 | S_SIS | 1 | pump_nr | 1 | Pump[x] | ?
47 | 1.705 | ['LSA-'] | 1.705 | Flow Switch H2O2 | S_LIMIT_SWITCH | 5
48 | 1.706 | ['V'] | 1.706 | Control valve compressed air | S_VALVE_FLAP | 9
49 | 1.707 | ['V', 'YC'] | 1.707 | Needle valve compressed air | S_MOTOR1 | 12
50 | 1.708 | ['FICA±'] | 1.708 | Flow switch compressed air | S_LIMIT_HI_LO | 12
51 | 1.71 | ['M', 'P', 'SC'] | 1.710 | Peristaltic pump | S_PUMP_TEST | 1 | S_SIS | 1 | pump_nr | 2 | Pump[x] | ?
52 | 1.715 | ['LSA-'] | 1.715 | Flow Switch H2O2 | S_LIMIT_SWITCH | 6
53 | 1.716 | ['V'] | 1.716 | Control valve compressed air | S_VALVE_FLAP | 10
54 | 1.717 | ['V', 'YC'] | 1.717 | Needle valve compressed air | S_MOTOR1 | 13
55 | 1.718 | ['FICA±'] | 1.718 | Flow switch compressed air | S_LIMIT_HI_LO | 13
56 | 1.72 | ['M', 'P', 'SC'] | 1.720 | Peristaltic pump | S_PUMP_TEST | 1 | S_SIS | 1 | pump_nr | 3 | Pump[x] | ?
57 | 1.725 | ['LSA-'] | 1.725 | Flow Switch H2O2 | S_LIMIT_SWITCH | 7
58 | 1.726 | ['V'] | 1.726 | Control valve compressed air | S_VALVE_FLAP | 11
59 | 1.727 | ['V', 'YC'] | 1.727 | Needle valve compressed air | S_MOTOR1 | 14
60 | 1.728 | ['FICA±'] | 1.728 | Flow switch compressed air | S_LIMIT_HI_LO | 14
61 | 1.746 | ['V'] | 1.746 | Control valve compressed air | S_VALVE_FLAP | 12
62 | 1.8 | ['TICA±'] | 1.800 | Temperature sensor | S_LIMIT_HI_LO | 15
63 | 1.81 | ['MIA±'] | 1.810 | Humidity sensor | S_LIMIT_HI_LO | 16
64 | 1.815 | ['WICA±'] | 1.815 | Weight scale | S_WEIGHT_SCALE2_NG | 1 | A_DOSING_UNIT | 1 | S_LIMIT_HI_LO | 18
65 | 1.816 | ['WICA±'] | 1.816 | Weight scale | S_WEIGHT_SCALE2_NG | 2 | A_DOSING_UNIT | 2 | S_LIMIT_HI_LO | 20
66 | 1.82 | ['SIA±'] | 1.820 | Air speed sensor | S_LIMIT_HI_LO | 21
67 | 1.825 | ['FIA+', 'H', 'YC'] | 1.825 | Flow rate sensor | S_MOTOR1 | 15 | S_REG_CONT | 4 | S_LIMIT_HI_LO | 26
68 | 1.83 | ['M', 'P', 'QIA+', 'XA'] | 1.830 | H2O2 LC sensor | S_LIMIT_HI_LO | 22
69 | 1.831 | ['GSA+', 'GSA-', 'V', 'Y'] | 1.831 | H2O2 LC valve | S_VALVE_FLAP | 13
70 | 1.832 | ['QIA-'] | 1.832 | H2O2 HC sensor | S_LIMIT_HI_LO | 23
71 | 1.833 | ['QSA+'] | 1.833 | TLV H2O2 LC Sensor | S_LIMIT_HI_LO | 24
72 | 1.834 | ['QSA+'] | 1.834 | TLV H2O2 LC Sensor | S_LIMIT_HI_LO | 25
73 | 1.84 | ['PDICA±'] | 1.840 | Differential pressure sensor | S_LIMIT_HI_LO | 26
74 | 1.842 | ['PDI'] | 1.842 | Differential pressure sensor | S_LIMIT_HI_LO | 27
75 | 1.853 | ['PSA-', 'V'] | 1.853 | Pressure reduction 1 | S_LIMIT_SWITCH | 8
76 | 1.86 | ['V'] | 1.860 | Control valves including 3-way valve | S_LIMIT_ON_OFF | 2 | S_LIMIT_HI_LO | 26
77 | 1.861 | ['V'] | 1.861 | Pressure sensor | S_VALVE_FLAP | 14
78 | 1.865 | ['PSA-', 'V'] | 1.865 | Inflatable Gasket | S_GASKET | 1 | S_LIMIT_HI_LO | 48
79 | 1.866 | ['PSA-', 'V'] | 1.866 | Inflatable Gasket | S_GASKET | 2 | S_LIMIT_HI_LO | 49
80 | 1.867 | ['PSA-', 'V'] | 1.867 | Inflatable Gasket | S_GASKET | 3 | S_LIMIT_HI_LO | 50
81 | 1.868 | ['PSA-', 'V'] | 1.868 | Inflatable Gasket | S_GASKET | 4 | S_LIMIT_HI_LO | 51
82 | 1.869 | ['PSA-', 'V'] | 1.869 | Inflatable Gasket | S_GASKET | 5 | S_LIMIT_HI_LO | 52
83 | 1.87 | ['PSA-', 'V'] | 1.870 | Inflatable Gasket | S_GASKET | 6 | S_LIMIT_HI_LO | 53
84 | 1.901 | ['GZA-'] | 1.901 | Safety door | S_LIMIT_SWITCH | 9 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 1
85 | 1.902 | ['GZA-'] | 1.902 | Safety door | S_LIMIT_SWITCH | 10 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 2
86 | 1.903 | ['GZA-'] | 1.903 | Safety door | S_LIMIT_SWITCH | 11 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 3
87 | 1.904 | ['GZA-'] | 1.904 | Safety door | S_LIMIT_SWITCH | 12 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 4
88 | 1.905 | ['GZA-'] | 1.905 | Safety door | S_LIMIT_SWITCH | 13 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 5
89 | 1.906 | ['GZA-'] | 1.906 | Safety door | S_LIMIT_SWITCH | 14 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 6
90 | 1.911 | ['GSA-'] | 1.911 | Service cover | S_LIMIT_SWITCH | 15 | S_GASKET | 2 | A_GASKET_SERVICE_COVER | 1
91 | 1.912 | ['GSA-'] | 1.912 | Service cover | S_LIMIT_SWITCH | 16 | S_GASKET | 2 | A_GASKET_SERVICE_COVER | 2
92 | 1.913 | ['GSA-'] | 1.913 | Service cover | S_LIMIT_SWITCH | 17 | S_GASKET | 2 | A_GASKET_SERVICE_COVER | 3
93 | 1.914 | ['GSA-'] | 1.914 | Service cover | S_LIMIT_SWITCH | 18 | S_GASKET | 2 | A_GASKET_SERVICE_COVER | 4
94 | 1.915 | ['GSA-'] | 1.915 | Service cover | S_LIMIT_SWITCH | 19 | S_GASKET | 3 | A_GASKET_SERVICE_COVER | 5
95 | 1.916 | ['GSA-'] | 1.916 | Service cover | S_LIMIT_SWITCH | 20 | S_GASKET | 3 | A_GASKET_SERVICE_COVER | 6
96 | 1.917 | ['GSA-'] | 1.917 | Service cover | S_LIMIT_SWITCH | 21 | S_GASKET | 3 | A_GASKET_SERVICE_COVER | 7
97 | 1.918 | ['GSA-'] | 1.918 | Service cover | S_LIMIT_SWITCH | 22 | S_GASKET | 3 | A_GASKET_SERVICE_COVER | 8
98 | 1.919 | ['GSA-'] | 1.919 | Service cover | S_LIMIT_SWITCH | 23 | S_GASKET | 3 | A_GASKET_SERVICE_COVER | 9
99 | 1.921 | ['GZA-'] | 1.921 | Mousehole door | S_LIMIT_SWITCH | 24 | S_GASKET | 4 | A_GASKET_MOUSEHOLE_DOOR | 1
100 | 1.922 | ['GZA-'] | 1.922 | Mousehole door | S_LIMIT_SWITCH | 25 | S_GASKET | 5 | A_GASKET_MOUSEHOLE_DOOR | 2
101 | 1.923 | ['GZA-'] | 1.923 | Mousehole door | S_LIMIT_SWITCH | 26 | S_GASKET | 6 | A_GASKET_MOUSEHOLE_DOOR | 3
102 | 1.924 | ['GZA-'] | 1.924 | Mousehole door | S_LIMIT_SWITCH | 27 | S_GASKET | 6 | A_GASKET_MOUSEHOLE_DOOR | 4
103 | 1.931 | ['GZA-'] | 1.931 | Safety windows | S_LIMIT_SWITCH | 28
104 | 1.932 | ['GZA-'] | 1.932 | Safety windows | S_LIMIT_SWITCH | 29
105 | 1.941 | ['GZA-'] | 1.941 | Safety front door | S_LIMIT_SWITCH | 30
106 | 1.942 | ['GZA-'] | 1.942 | Safety front door | S_LIMIT_SWITCH | 31
107 | 1.943 | ['GZA-'] | 1.943 | Safety front door | S_LIMIT_SWITCH | 32
108 | 1.944 | ['GZA-'] | 1.944 | Safety front door | S_LIMIT_SWITCH | 33
109 | 1.945 | ['GZA-'] | 1.945 | Safety front door | S_LIMIT_SWITCH | 34
110 | 1.946 | ['GZA-'] | 1.946 | Safety front door | S_LIMIT_SWITCH | 35
111 | 1.961 | ['GZA-'] | 1.961 | Laser Scanner | S_LIMIT_SWITCH | 36
112 | 1.962 | ['GZA-'] | 1.962 | Laser Scanner | S_LIMIT_SWITCH | 37
113 | 1.963 | ['GZA-'] | 1.963 | Laser Scanner | S_LIMIT_SWITCH | 38
114 | 1.99 | ['L'] | 1.990 | Lighting | S_ELMT_ON_OFF | 6
115 | 1.991 | ['L'] | 1.991 | Alarm lights | S_ELMT_ON_OFF | 7
116 | 2.2 | ['M', 'SC', 'V', 'XA'] | 2.200 | Recirculation fan | S_MOTOR1 | 16
117 | 2.208 | ['PDI'] | 2.208 | Diferential pressure sensor | S_LIMIT_HI_LO | 28
118 | 2.21 | ['M', 'SC', 'V', 'XA'] | 2.210 | Recirculation fan | S_MOTOR1 | 17
119 | 2.218 | ['PDI'] | 2.218 | Diferential pressure sensor | S_LIMIT_HI_LO | 29
120 | 2.3 | ['FA-', 'QIA+', 'XA'] | 2.300 | Particle counter | S_PMS_MODBUS_TCP | 5
121 | 2.304 | ['M', 'P'] | 2.304 | Vacuum pump | S_ELMT_ON_OFF | 8
122 | 2.308 | ['FSA-'] | 2.308 | Flow-Switch | S_LIMIT_SWITCH | 39
123 | 2.35 | ['P', 'XA'] | 2.350 | Air sampler | S_AAS_MAS_TCP | 4
124 | 2.7 | ['M', 'P', 'SC'] | 2.700 | Peristaltic pump | S_PUMP_TEST | 2 | S_SIS | 2 | pump_nr | 4 | Pump[x] | ?
125 | 2.705 | ['LSA-'] | 2.705 | Flow Switch H2O2 | S_LIMIT_SWITCH | 40
126 | 2.706 | ['V'] | 2.706 | Control valve compressed air | S_VALVE_FLAP | 15
127 | 2.707 | ['V', 'YC'] | 2.707 | Needle valve compressed air | S_MOTOR1 | 18
128 | 2.708 | ['FICA±'] | 2.708 | Flow switch compressed air | S_LIMIT_HI_LO | 30
129 | 2.71 | ['M', 'P', 'SC'] | 2.710 | Peristaltic pump | S_PUMP_TEST | 2 | S_SIS | 2 | pump_nr | 5 | Pump[x] | ?
130 | 2.715 | ['LSA-'] | 2.715 | Flow Switch H2O2 | S_LIMIT_SWITCH | 41
131 | 2.716 | ['V'] | 2.716 | Control valve compressed air | S_VALVE_FLAP | 16
132 | 2.717 | ['V', 'YC'] | 2.717 | Needle valve compressed air | S_MOTOR1 | 19
133 | 2.718 | ['FICA±'] | 2.718 | Flow switch compressed air | S_LIMIT_HI_LO | 31
134 | 2.72 | ['M', 'P', 'SC'] | 2.720 | Peristaltic pump | S_PUMP_TEST | 2 | S_SIS | 2 | pump_nr | 6 | Pump[x] | ?
135 | 2.725 | ['LSA-'] | 2.725 | Flow Switch H2O2 | S_LIMIT_SWITCH | 42
136 | 2.727 | ['V', 'YC'] | 2.727 | Needle valve compressed air | S_MOTOR1 | 20
137 | 2.728 | ['FICA±'] | 2.728 | Flow switch compressed air | S_LIMIT_HI_LO | 32
138 | 2.99 | ['L'] | 2.990 | Lighting | S_ELMT_ON_OFF | 9
139 | AHU01 | AHU01 |  | Leader/Follower AHU 01 1.800 - (1.655-1.680 | S_REG_CONT | 5 | S_LIMIT_HI_LO | 15 | S_REG_CONT | 2 | S_REG_CONT | 3
140 | 1.800_precon | [702] [17°C < 28°C] |  | Temperature sensor | S_LIMIT_HI_LO | 33
141 | 1.800_deco | [118] [17°C < 28°C] |  | Temperature sensor | S_LIMIT_HI_LO | 34
142 | 1.800_pro | [114] [15°C < 21°C] |  | Temperature sensor | S_LIMIT_HI_LO | 35
143 | 1.800_aer1 | [708] [30°C < 40°C] |  | Temperature sensor | S_LIMIT_HI_LO | 36
144 | 1.810_pro | [114] [< 100%RH] |  | Humidity sensor | S_LIMIT_HI_LO | 37
145 | 1.810_precon | [702] [15%RH < 20%RH] |  | Humidity sensor | S_LIMIT_HI_LO | 38
146 | 1.810_deco | [118] [< 100%RH] |  | Humidity sensor | S_LIMIT_HI_LO | 39
147 | 1.820_pro | [114] [> 0.45m/s] |  | Air velocity sensor | S_LIMIT_HI_LO | 40
148 | 1.820_deco | [118] [> 0.20m/s] |  | Air velocity sensor | S_LIMIT_HI_LO | 41
149 | 1.820_aer2 | [709] [> 0.45m/s] |  | Air velocity sensor | S_LIMIT_HI_LO | 42
150 | 1.825_leak | LEAK |  | Flow rate sensor | S_LIMIT_HI_LO | 43 | S_LEAK | 1
151 | 1.840_prod | [114] [>30Pa] |  | Differencial pressure sensor | S_LIMIT_HI_LO | 44
152 | 1.840_deco | [118] [>15Pa] |  | Differencial pressure sensor | S_LIMIT_HI_LO | 45
153 | 1.840_leak | [108] [60Pa] |  | Differencial pressure sensor | S_LIMIT_HI_LO | 46
154 | 1.840_emy | [105] [<-200Pa >200Pa] |  | Differencial pressure sensor | S_LIMIT_HI_LO | 47
155 | 1.55 | ['GIA', 'K', 'Y', 'YC'] |  | Exhaust air flap | S_LIMIT_HI_LO | 6 | S_MOTOR1 | 7
156 | 1.555 | ['GIA', 'V', 'Y', 'YC'] |  | Exhaust bypass valve | S_LIMIT_HI_LO | 7 | S_MOTOR1 | 8
157 | 1.56 | ['GIA', 'K', 'Y', 'YC'] |  | Exhaust air flap | S_LIMIT_HI_LO | 9 | S_MOTOR1 | 9
158 | 1.865 | ['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 48 | S_GASKET | 1
159 | 1.866 | ['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 49 | S_GASKET | 2
160 | 1.867 | ['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 50 | S_GASKET | 3
161 | 1.868 | ['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 51 | S_GASKET | 4
162 | 1.869 | ['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 52 | S_GASKET | 5
163 | 1.87 | ['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 53 | S_GASKET | 6