## Sheet1
Prop_PID_Element | sPID | Tag_Number_Definition | SWM | SWM_Nr | Cx1 | Cx1_Nr | Cx2 | Cx2_Nr | Cx3 | Cx3_Nr | Cx4 | Cx4_Nr | Element_Description
['M', 'SC', 'V', 'XA'] | 1.100 | Intake air fan | S_MOTOR1 | 1
['PDI'] | 1.108 | Diferential pressure sensor | S_LIMIT_HI_LO | 1
['M', 'SC', 'TSA+', 'V'] | 1.150 | Exhaust air fan | S_DRIVE | 1 | S_MOTOR1 | 2 | S_REG_CONT | 1 | S_LIMIT_HI_LO | 23
['PDI'] | 1.158 | Diferential pressure sensor | S_LIMIT_HI_LO | 2
['M', 'SC', 'V', 'XA'] | 1.160 | Exhaust air fan | S_MOTOR1 | 3
['M', 'SC', 'V', 'XA'] | 1.200 | Recirculation fan | S_MOTOR1 | 4
['PDI'] | 1.208 | Diferential pressure sensor | S_LIMIT_HI_LO | 3
['M', 'SC', 'V', 'XA'] | 1.210 | Recirculation fan | S_MOTOR1 | 5
['PDI'] | 1.218 | Diferential pressure sensor | S_LIMIT_HI_LO | 4
['M', 'SC', 'V', 'XA'] | 1.240 | Recirculation fan | S_MOTOR1 | 6
['PDI'] | 1.248 | Diferential pressure sensor | S_LIMIT_HI_LO | 5
['FA-', 'QIA+', 'XA'] | 1.300 | Particle counter | S_PMS_MODBUS_TCP | 1
['M', 'P'] | 1.304 | Vacuum pump | S_ELMT_ON_OFF | 1
['GSA+', 'GSA-', 'V', 'Y'] | 1.305 | 3-way valve | S_VALVE_FLAP | 1
['FSA-'] | 1.308 | Flow-Switch | S_LIMIT_SWITCH | 1
['FA-', 'QIA+', 'XA'] | 1.310 | Particle counter | S_PMS_MODBUS_TCP | 2
['M', 'P'] | 1.314 | Vacuum pump | S_ELMT_ON_OFF | 2
['GSA+', 'GSA-', 'V', 'Y'] | 1.315 | 3-way valve | S_VALVE_FLAP | 2
['FSA-'] | 1.318 | Flow-Switch | S_LIMIT_SWITCH | 2
['FA-', 'QIA+', 'XA'] | 1.320 | Particle counter | S_PMS_MODBUS_TCP | 3
['M', 'P'] | 1.324 | Vacuum pump | S_ELMT_ON_OFF | 3
['GSA+', 'GSA-', 'V', 'Y'] | 1.325 | 3-way valve | S_VALVE_FLAP | 3
['FSA-'] | 1.328 | Flow-Switch | S_LIMIT_SWITCH | 3
['FA-', 'QIA+', 'XA'] | 1.330 | Particle counter | S_PMS_MODBUS_TCP | 4
['M', 'P'] | 1.334 | Vacuum pump | S_ELMT_ON_OFF | 4
['GSA+', 'GSA-', 'V', 'Y'] | 1.335 | 3-way valve | S_VALVE_FLAP | 4
['FSA-'] | 1.338 | Flow-Switch | S_LIMIT_SWITCH | 4
['P', 'XA'] | 1.350 | Air sampler | S_AAS_MAS_TCP | 1
['P', 'XA'] | 1.360 | Air sampler | S_AAS_MAS_TCP | 2
['P', 'XA'] | 1.370 | Air sampler | S_AAS_MAS_TCP | 3
['GIA+', 'GIA-', 'M', 'SC', 'XA'] | 1.400 | Automatic Mousehole
['GIA+', 'GIA-', 'M', 'SC', 'XA'] | 1.410
['GSA+', 'GSA-', 'K', 'Y'] | 1.500 | Supply air flap | S_VALVE_FLAP | 5
['GSA+', 'GSA-', 'K', 'Y'] | 1.510 | Flap | S_VALVE_FLAP | 6
['GSA+', 'GSA-', 'K', 'Y'] | 1.520 | Flap | S_VALVE_FLAP | 7
['GIA', 'K', 'Y', 'YC'] | 1.550 | Exhaust air flap | S_MOTOR1 | 7
['GIA', 'V', 'Y', 'YC'] | 1.555 | Exhaust bypass valve | S_MOTOR1 | 8
['PDIS'] | 1.558 | Diferential pressure sensor | S_LIMIT_HI_LO | 6
['GIA', 'K', 'Y', 'YC'] | 1.560 | Exhaust air flap | S_MOTOR1 | 9
['PDIS'] | 1.568 | Diferential pressure sensor | S_LIMIT_HI_LO | 7
['GSA+', 'GSA-', 'K', 'Y'] | 1.570 | Flap | S_VALVE_FLAP | 8
['M', 'P'] | 1.651 | Circulating pump | S_ELMT_ON_OFF | 5
['H', 'M', 'NC'] | 1.655 | Control valve | S_MOTOR1 | 10 | S_REG_CONT | 2 | S_LIMIT_HI_LO | 8
['EC', 'TSA+'] | 1.680 | Electric heating | S_MOTOR1 | 11 | S_REG_CONT | 3 | S_LIMIT_HI_LO | 8
['TIC'] | 1.688 | Temperature sensor | S_LIMIT_HI_LO | 8
['T', 'XA'] | 1.690 | Dryer / Humidifier | S_LIMIT_ON_OFF | 1 | S_LIMIT_HI_LO | ?
['M', 'P', 'SC'] | 1.700 | Peristaltic pump | S_SIS | 1 | A_PUMPS | 1
['LSA-'] | 1.705 | Flow Switch H2O2 | S_LIMIT_SWITCH | 5
['V'] | 1.706 | Control valve compressed air | S_VALVE_FLAP | 9
['V', 'YC'] | 1.707 | Needle valve compressed air | S_MOTOR1 | 12
['FICA±'] | 1.708 | Flow switch compressed air | S_LIMIT_HI_LO | 9
['M', 'P', 'SC'] | 1.710 | Peristaltic pump | S_SIS | 1 | A_PUMPS | 2
['LSA-'] | 1.715 | Flow Switch H2O2 | S_LIMIT_SWITCH | 6
['V'] | 1.716 | Control valve compressed air | S_VALVE_FLAP | 10
['V', 'YC'] | 1.717 | Needle valve compressed air | S_MOTOR1 | 13
['FICA±'] | 1.718 | Flow switch compressed air | S_LIMIT_HI_LO | 10
['M', 'P', 'SC'] | 1.720 | Peristaltic pump | S_SIS | 1 | A_PUMPS | 3
['LSA-'] | 1.725 | Flow Switch H2O2 | S_LIMIT_SWITCH | 7
['V'] | 1.726 | Control valve compressed air | S_VALVE_FLAP | 11
['V', 'YC'] | 1.727 | Needle valve compressed air | S_MOTOR1 | 14
['FICA±'] | 1.728 | Flow switch compressed air | S_LIMIT_HI_LO | 11
['V'] | 1.746 | Control valve compressed air | S_VALVE_FLAP | 12
['TICA±'] | 1.800 | Temperature sensor | S_LIMIT_HI_LO | 12
['MIA±'] | 1.810 | Humidity sensor | S_LIMIT_HI_LO | 13
['WICA±'] | 1.815 | Weight scale | S_WEIGHT_SCALE2_NG | 1 | A_DOSING_UNIT | 1 | S_LIMIT_HI_LO | 15
['WICA±'] | 1.816 | Weight scale | S_WEIGHT_SCALE2_NG | 2 | A_DOSING_UNIT | 2 | S_LIMIT_HI_LO | 17
['SIA±'] | 1.820 | Air speed sensor | S_LIMIT_HI_LO | 18
['FIA+', 'H', 'YC'] | 1.825 | Flow rate sensor | S_MOTOR1 | 15 | S_REG_CONT | 4 | S_LIMIT_HI_LO | 23
['M', 'P', 'QIA+', 'XA'] | 1.830 | H2O2 LC sensor | S_LIMIT_HI_LO | 19
['GSA+', 'GSA-', 'V', 'Y'] | 1.831 | H2O2 LC valve | S_VALVE_FLAP | 13
['QIA-'] | 1.832 | H2O2 HC sensor | S_LIMIT_HI_LO | 20
['QSA+'] | 1.833 | TLV H2O2 LC Sensor | S_LIMIT_HI_LO | 21
['QSA+'] | 1.834 | TLV H2O2 LC Sensor | S_LIMIT_HI_LO | 22
['PDICA±'] | 1.840 | Differential pressure sensor | S_LIMIT_HI_LO | 23
['PDI'] | 1.842 | Differential pressure sensor | S_LIMIT_HI_LO | 24
['PSA-', 'V'] | 1.853 | Pressure reduction 1 | S_LIMIT_SWITCH | 8
['V'] | 1.860 | Control valves including 3-way valve | S_LIMIT_ON_OFF | 2 | S_LIMIT_HI_LO | ?
['V'] | 1.861 | Pressure sensor | S_VALVE_FLAP | 14
['PSA-', 'V'] | 1.865 | Inflatable Gasket | S_GASKET | 1 | S_LIMIT_HI_LO | 45
['PSA-', 'V'] | 1.866 | Inflatable Gasket | S_GASKET | 2 | S_LIMIT_HI_LO | 46
['PSA-', 'V'] | 1.867 | Inflatable Gasket | S_GASKET | 3 | S_LIMIT_HI_LO | 47
['PSA-', 'V'] | 1.868 | Inflatable Gasket | S_GASKET | 4 | S_LIMIT_HI_LO | 48
['PSA-', 'V'] | 1.869 | Inflatable Gasket | S_GASKET | 5 | S_LIMIT_HI_LO | 49
['PSA-', 'V'] | 1.870 | Inflatable Gasket | S_GASKET | 6 | S_LIMIT_HI_LO | 50
['GZA-'] | 1.901 | Safety door | S_LIMIT_SWITCH | 9 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 1
['GZA-'] | 1.902 | Safety door | S_LIMIT_SWITCH | 10 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 2
['GZA-'] | 1.903 | Safety door | S_LIMIT_SWITCH | 11 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 3
['GZA-'] | 1.904 | Safety door | S_LIMIT_SWITCH | 12 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 4
['GZA-'] | 1.905 | Safety door | S_LIMIT_SWITCH | 13 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 5
['GZA-'] | 1.906 | Safety door | S_LIMIT_SWITCH | 14 | S_GASKET | 1 | A_GASKET_SAFETY_DOOR | 6
['GSA-'] | 1.911 | Service cover | S_LIMIT_SWITCH | 15 | S_GASKET | 2 | A_GASKET_SERVICE_COVER | 1
['GSA-'] | 1.912 | Service cover | S_LIMIT_SWITCH | 16 | S_GASKET | 2 | A_GASKET_SERVICE_COVER | 2
['GSA-'] | 1.913 | Service cover | S_LIMIT_SWITCH | 17 | S_GASKET | 2 | A_GASKET_SERVICE_COVER | 3
['GSA-'] | 1.914 | Service cover | S_LIMIT_SWITCH | 18 | S_GASKET | 2 | A_GASKET_SERVICE_COVER | 4
['GSA-'] | 1.915 | Service cover | S_LIMIT_SWITCH | 19 | S_GASKET | 3 | A_GASKET_SERVICE_COVER | 5
['GSA-'] | 1.916 | Service cover | S_LIMIT_SWITCH | 20 | S_GASKET | 3 | A_GASKET_SERVICE_COVER | 6
['GSA-'] | 1.917 | Service cover | S_LIMIT_SWITCH | 21 | S_GASKET | 3 | A_GASKET_SERVICE_COVER | 7
['GSA-'] | 1.918 | Service cover | S_LIMIT_SWITCH | 22 | S_GASKET | 3 | A_GASKET_SERVICE_COVER | 8
['GSA-'] | 1.919 | Service cover | S_LIMIT_SWITCH | 23 | S_GASKET | 3 | A_GASKET_SERVICE_COVER | 9
['GZA-'] | 1.921 | Mousehole door | S_LIMIT_SWITCH | 24 | S_GASKET | 4 | A_GASKET_MOUSEHOLE_DOOR | 1
['GZA-'] | 1.922 | Mousehole door | S_LIMIT_SWITCH | 25 | S_GASKET | 5 | A_GASKET_MOUSEHOLE_DOOR | 2
['GZA-'] | 1.923 | Mousehole door | S_LIMIT_SWITCH | 26 | S_GASKET | 6 | A_GASKET_MOUSEHOLE_DOOR | 3
['GZA-'] | 1.924 | Mousehole door | S_LIMIT_SWITCH | 27 | S_GASKET | 6 | A_GASKET_MOUSEHOLE_DOOR | 4
['GZA-'] | 1.931 | Safety windows | S_LIMIT_SWITCH | 28
['GZA-'] | 1.932 | Safety windows | S_LIMIT_SWITCH | 29
['GZA-'] | 1.941 | Safety front door | S_LIMIT_SWITCH | 30
['GZA-'] | 1.942 | Safety front door | S_LIMIT_SWITCH | 31
['GZA-'] | 1.943 | Safety front door | S_LIMIT_SWITCH | 32
['GZA-'] | 1.944 | Safety front door | S_LIMIT_SWITCH | 33
['GZA-'] | 1.945 | Safety front door | S_LIMIT_SWITCH | 34
['GZA-'] | 1.946 | Safety front door | S_LIMIT_SWITCH | 35
['GZA-'] | 1.961 | Laser Scanner | S_LIMIT_SWITCH | 36
['GZA-'] | 1.962 | Laser Scanner | S_LIMIT_SWITCH | 37
['GZA-'] | 1.963 | Laser Scanner | S_LIMIT_SWITCH | 38
['L'] | 1.990 | Lighting | S_ELMT_ON_OFF | 6
['L'] | 1.991 | Alarm lights | S_ELMT_ON_OFF | 7
['M', 'SC', 'V', 'XA'] | 2.200 | Recirculation fan | S_MOTOR1 | 16
['PDI'] | 2.208 | Diferential pressure sensor | S_LIMIT_HI_LO | 25
['M', 'SC', 'V', 'XA'] | 2.210 | Recirculation fan | S_MOTOR1 | 17
['PDI'] | 2.218 | Diferential pressure sensor | S_LIMIT_HI_LO | 26
['FA-', 'QIA+', 'XA'] | 2.300 | Particle counter | S_PMS_MODBUS_TCP | 5
['M', 'P'] | 2.304 | Vacuum pump | S_ELMT_ON_OFF | 8
['FSA-'] | 2.308 | Flow-Switch | S_LIMIT_SWITCH | 39
['P', 'XA'] | 2.350 | Air sampler | S_AAS_MAS_TCP | 4
['M', 'P', 'SC'] | 2.700 | Peristaltic pump | S_SIS | 2 | A_PUMPS | 4
['LSA-'] | 2.705 | Flow Switch H2O2 | S_LIMIT_SWITCH | 40
['V'] | 2.706 | Control valve compressed air | S_VALVE_FLAP | 15
['V', 'YC'] | 2.707 | Needle valve compressed air | S_MOTOR1 | 18
['FICA±'] | 2.708 | Flow switch compressed air | S_LIMIT_HI_LO | 27
['M', 'P', 'SC'] | 2.710 | Peristaltic pump | S_SIS | 2 | A_PUMPS | 5
['LSA-'] | 2.715 | Flow Switch H2O2 | S_LIMIT_SWITCH | 41
['V'] | 2.716 | Control valve compressed air | S_VALVE_FLAP | 16
['V', 'YC'] | 2.717 | Needle valve compressed air | S_MOTOR1 | 19
['FICA±'] | 2.718 | Flow switch compressed air | S_LIMIT_HI_LO | 28
['M', 'P', 'SC'] | 2.720 | Peristaltic pump | S_SIS | 2 | A_PUMPS | 6
['LSA-'] | 2.725 | Flow Switch H2O2 | S_LIMIT_SWITCH | 42
['V', 'YC'] | 2.727 | Needle valve compressed air | S_MOTOR1 | 20
['FICA±'] | 2.728 | Flow switch compressed air | S_LIMIT_HI_LO | 29
['L'] | 2.990 | Lighting | S_ELMT_ON_OFF | 9
AHU01 |  | Leader/Follower AHU 01 1.800 - (1.655-1.680 | S_REG_CONT | 5 | S_LIMIT_HI_LO | 12 | S_REG_CONT | 2 | S_REG_CONT | 3
[702] [17°C < 28°C] |  | Temperature sensor | S_LIMIT_HI_LO | 30
[118] [17°C < 28°C] |  | Temperature sensor | S_LIMIT_HI_LO | 31
[114] [15°C < 21°C] |  | Temperature sensor | S_LIMIT_HI_LO | 32
[708] [30°C < 40°C] |  | Temperature sensor | S_LIMIT_HI_LO | 33
[114] [< 100%RH] |  | Humidity sensor | S_LIMIT_HI_LO | 34
[702] [15%RH < 20%RH] |  | Humidity sensor | S_LIMIT_HI_LO | 35
[118] [< 100%RH] |  | Humidity sensor | S_LIMIT_HI_LO | 36
[114] [> 0.45m/s] |  | Air velocity sensor | S_LIMIT_HI_LO | 37
[118] [> 0.20m/s] |  | Air velocity sensor | S_LIMIT_HI_LO | 38
[709] [> 0.45m/s] |  | Air velocity sensor | S_LIMIT_HI_LO | 39
LEAK |  | Flow rate sensor | S_LIMIT_HI_LO | 40 | S_LEAK | 1
[114] [>30Pa] |  | Differencial pressure sensor | S_LIMIT_HI_LO | 41
[118] [>15Pa] |  | Differencial pressure sensor | S_LIMIT_HI_LO | 42
[108] [60Pa] |  | Differencial pressure sensor | S_LIMIT_HI_LO | 43
[105] [<-200Pa >200Pa] |  | Differencial pressure sensor | S_LIMIT_HI_LO | 44
[SIS] |  | SIS MODULE | S_SIS | 1 | A_DOSING_UNIT | 1 | S_LIMIT_HI_LO | 15 | S_LIMIT_HI_LO | 12 | S_LIMIT_HI_LO | 13
[PTEST] |  | PUMP TEST MODULE | S_PUMP_TEST | 1 | A_DOSING_UNIT | 1
[DU] |  | DOSING UNIT MODULE | A_DOSING_UNIT | 1 | S_WEIGHT_SCALE2_NG | 1 | S_SIS | 1 | S_PUMP_TEST | 1
[SIS] |  | SIS MODULE | S_SIS | 2 | A_DOSING_UNIT | 2 | S_LIMIT_HI_LO | 17 | S_LIMIT_HI_LO | 12 | S_LIMIT_HI_LO | 13
[PTEST] |  | PUMP TEST MODULE | S_PUMP_TEST | 2 | A_DOSING_UNIT | 2
[DU] |  | DOSING UNIT MODULE | A_DOSING_UNIT | 2 | S_WEIGHT_SCALE2_NG | 2 | S_SIS | 2 | S_PUMP_TEST | 2
['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 45 | S_GASKET | 1
['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 46 | S_GASKET | 2
['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 47 | S_GASKET | 3
['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 48 | S_GASKET | 4
['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 49 | S_GASKET | 5
['PSA-', 'V'] |  | Inflatable Gasket | S_LIMIT_HI_LO | 50 | S_GASKET | 6